## Slide 1
AREAL Linear Accelerator cooling system design.
Vardanyan Vahagn

## Slide 2
AREAL Linear Accelerator Cooling system's Specification.
Significance.
Linear accelerator consists of various types of equipment. During operation of the accelerator, many of these equipment produce large amounts of heat. For the normal operation of the Linear Accelerator required to remove heat. Heat removal from the system can be performed using different cooling systems.
For selected accelerator cooling system should be taken into account accelerator equipment specifications.

## Slide 3
GUN
Quadruple Magnets
S-Band
accel. sections
Beam dumps

## Slide 4
Basic requirements for the cooling system.
General requirements.
1. High productivity.
2. Economic efficiency.
3. Safety.
4. High Automation.
5. Easy maintenance.
Parameters.
Parameters of the equipment cooling system.
Equipment Quantity.
Features of the building.

## Slide 5
AREAL Cooling System features.
 | Gun | Klystron | Beam Dumps, Magnet | RF cavity
Cooling capacity (W) | 1600 | 150 | 150 | 14
Temperature (0C) | 42.5 | 42.5 | 30 | 30
Temperature Stability (0C) | +/-0.1 | +/-0.1 | +/-1 | +/-0.1
Water Flow rate (l/min) | 22 | 3.6 | 3.6 | 22
Pressure | Not exceed 4.2kg/cm2 |  |  | 

## Slide 7
Accel. Sec. 1.
Accel. Sec. 2.

## Slide 8
Automation of the cooling system.

## Slide 9
Water de-ionizer
flow controller
Electric Valves
Temperature Sensors
Water Chillers

## Slide 10: AREAL Cooling System 3D Model.

## Slide 11
Cooling Equipment Room
6 m2

## Slide 12
Water de-ionizer
Heated Water
Frozen Water.
Water Chillers

## Slide 13
Test Bench Scheme.

## Slide 14
Software

## Slide 15: Thanks for listening.